## Single
Sample Number | Notes | Pump Setting S [%] | Pump Speed n [rpm] | Water Temperature T [°C] | Inlet Pressure P0 [kPa] | Pump 1 Pressure P1 [kPa] | Pump 2 Pressure P2 [kPa] | Motor 1 Torque t [Nm] | Flow Rate Q [l/s] | Operating Mode | Density of water rho [kg/m³] | Pump 1 Inlet Velocity [m/s] | Pump 1 Outlet Velocity [m/s] | Pump 2 Inlet Velocity [m/s] | Pump 2 Outlet Velocity [m/s] | Pump 1 Total Head [m] | Pump 2 Total Head [m] | Combined Total Head [m] | Pump 1 Hydraulic Power [W] | Pump 2 Hydraulic Power [W] | Total Hydraulic Power [W] | Pump 1 Mechanical Power [W] | Pump 1 Efficiency E1 [%] | Pump 2 Efficiency E2 [%] | Overall Efficiency Egr [%] | Walkthrough Questions Score [%]
1 |  | 70 | 1260 | 33.85 | 2.6254 | 31.0755 | 30.5454 | 0.34319 | 0.16992 | Single | 994.4837 | 0.39176 | 0.70645 |  |  | 3.0088 |  | 3.0088 | 4.9878 |  | 4.9878 | 45.2828 | 11.0149 |  | 11.0149
2 |  | 70 | 1260 | 33.8 | 2.6254 | 30.3435 | 30.3939 | 0.34164 | 0.20703 | Single | 994.5 | 0.47732 | 0.86074 |  |  | 2.9423 |  | 2.9423 | 5.9428 |  | 5.9428 | 45.0788 | 13.1831 |  | 13.1831
3 |  | 70 | 1260 | 33.85 | 2.4234 | 29.9648 | 29.8386 | 0.34474 | 0.20703 | Single | 994.4837 | 0.47732 | 0.86074 |  |  | 2.9242 |  | 2.9242 | 5.9062 |  | 5.9062 | 45.4868 | 12.9845 |  | 12.9845
4 |  | 70 | 1260 | 33.8 | 2.4739 | 29.4599 | 29.1822 | 0.35092 | 0.2832 | Single | 994.5 | 0.65294 | 1.1774 |  |  | 2.89 |  | 2.89 | 7.9849 |  | 7.9849 | 46.3027 | 17.2451 |  | 17.2451
5 |  | 70 | 1260 | 33.8 | 2.5244 | 28.3997 | 29.0308 | 0.34783 | 0.32031 | Single | 994.5 | 0.7385 | 1.3317 |  |  | 2.7898 |  | 2.7898 | 8.7181 |  | 8.7181 | 45.8947 | 18.996 |  | 18.996
6 |  | 70 | 1260 | 33.8 | 2.4739 | 26.6831 | 28.7278 | 0.3571 | 0.45312 | Single | 994.5 | 1.0447 | 1.8839 |  |  | 2.6817 |  | 2.6817 | 11.855 |  | 11.855 | 47.1186 | 25.16 |  | 25.16
7 |  | 70 | 1260 | 33.8 | 2.3729 | 23.6285 | 25.1432 | 0.36947 | 0.56641 | Single | 994.5 | 1.3059 | 2.3548 |  |  | 2.4494 |  | 2.4494 | 13.5352 |  | 13.5352 | 48.7504 | 27.7644 |  | 27.7644
8 |  | 70 | 1260 | 33.8 | 2.4739 | 22.0381 | 24.5373 | 0.37256 | 0.67969 | Single | 994.5 | 1.5671 | 2.8258 |  |  | 2.3622 |  | 2.3622 | 15.6637 |  | 15.6637 | 49.1583 | 31.8638 |  | 31.8638
9 |  | 70 | 1260 | 33.8 | 2.0195 | 19.2108 | 23.0731 | 0.37411 | 0.67969 | Single | 994.5 | 1.5671 | 2.8258 |  |  | 2.1189 |  | 2.1189 | 14.0509 |  | 14.0509 | 49.3623 | 28.4648 |  | 28.4648
10 |  | 70 | 1260 | 33.8 | 2.171 | 19.6147 | 22.7197 | 0.37411 | 0.7168 | Single | 994.5 | 1.6526 | 2.9801 |  |  | 2.1764 |  | 2.1764 | 15.22 |  | 15.22 | 49.3623 | 30.8333 |  | 30.8333
11 |  | 70 | 1260 | 33.8 | 2.2215 | 17.3427 | 21.407 | 0.38338 | 0.75391 | Single | 994.5 | 1.7382 | 3.1344 |  |  | 1.9717 |  | 1.9717 | 14.502 |  | 14.502 | 50.5862 | 28.6679 |  | 28.6679
12 |  | 70 | 1260 | 33.8 | 2.07 | 17.2922 | 23.78 | 0.38184 | 0.77344 | Single | 994.5 | 1.7832 | 3.2156 |  |  | 2.0002 |  | 2.0002 | 15.0931 |  | 15.0931 | 50.3822 | 29.9572 |  | 29.9572
13 |  | 70 | 1260 | 33.8 | 2.171 | 15.8028 | 20.2963 | 0.38493 | 0.79297 | Single | 994.5 | 1.8282 | 3.2968 |  |  | 1.8559 |  | 1.8559 | 14.3575 |  | 14.3575 | 50.7901 | 28.2683 |  | 28.2683
14 |  | 70 | 1260 | 33.85 | 2.1205 | 15.0708 | 19.1351 | 0.38647 | 0.81055 | Single | 994.4837 | 1.8688 | 3.3699 |  |  | 1.8032 |  | 1.8032 | 14.2592 |  | 14.2592 | 50.9941 | 27.9625 |  | 27.9625
15 |  | 70 | 1260 | 33.85 | 2.07 | 14.9698 | 18.2263 | 0.38802 | 0.83008 | Single | 994.4837 | 1.9138 | 3.4511 |  |  | 1.8176 |  | 1.8176 | 14.7192 |  | 14.7192 | 51.1981 | 28.7495 |  | 28.7495
16 |  | 70 | 1260 | 33.8 | 2.1205 | 15.1465 | 20.3468 | 0.38802 | 0.86719 | Single | 994.5 | 1.9993 | 3.6053 |  |  | 1.8689 |  | 1.8689 | 15.8119 |  | 15.8119 | 51.1981 | 30.8837 |  | 30.8837
17 |  | 70 | 1260 | 33.85 | 1.7166 | 14.6416 | 21.8614 | 0.39266 | 0.86719 | Single | 994.4837 | 1.9993 | 3.6053 |  |  | 1.8586 |  | 1.8586 | 15.7242 |  | 15.7242 | 51.81 | 30.3498 |  | 30.3498
18 |  | 70 | 1260 | 33.8 | 1.4642 | 12.4201 | 20.4478 | 0.38802 | 0.9043 | Single | 994.5 | 2.0849 | 3.7596 |  |  | 1.6969 |  | 1.6969 | 14.9704 |  | 14.9704 | 51.1981 | 29.2402 |  | 29.2402
19 |  | 70 | 1260 | 33.8 | 2.2215 | 13.5309 | 19.236 | 0.39111 | 0.9043 | Single | 994.5 | 2.0849 | 3.7596 |  |  | 1.7331 |  | 1.7331 | 15.29 |  | 15.29 | 51.6061 | 29.6283 |  | 29.6283
20 |  | 70 | 1260 | 33.8 | 1.969 | 11.789 | 17.0146 | 0.38802 | 0.92383 | Single | 994.5 | 2.1299 | 3.8408 |  |  | 1.6022 |  | 1.6022 | 14.4406 |  | 14.4406 | 51.1981 | 28.2054 |  | 28.2054
21 |  | 70 | 1260 | 33.8 | 2.07 | 13.3794 | 19.7409 | 0.39575 | 0.92383 | Single | 994.5 | 2.1299 | 3.8408 |  |  | 1.7549 |  | 1.7549 | 15.8166 |  | 15.8166 | 52.218 | 30.2895 |  | 30.2895
22 |  | 70 | 1260 | 33.8 | 1.969 | 12.6726 | 18.8321 | 0.3942 | 0.94336 | Single | 994.5 | 2.175 | 3.922 |  |  | 1.715 |  | 1.715 | 15.7842 |  | 15.7842 | 52.014 | 30.346 |  | 30.346

## Series
Sample Number | Notes | Pump Setting S [%] | Pump Speed n [rpm] | Water Temperature T [°C] | Inlet Pressure P0 [kPa] | Pump 1 Pressure P1 [kPa] | Pump 2 Pressure P2 [kPa] | Motor 1 Torque t [Nm] | Flow Rate Q [l/s] | Operating Mode | Density of water rho [kg/m³] | Pump 1 Inlet Velocity [m/s] | Pump 1 Outlet Velocity [m/s] | Pump 2 Inlet Velocity [m/s] | Pump 2 Outlet Velocity [m/s] | Pump 1 Total Head [m] | Pump 2 Total Head [m] | Combined Total Head [m] | Pump 1 Hydraulic Power [W] | Pump 2 Hydraulic Power [W] | Total Hydraulic Power [W] | Pump 1 Mechanical Power [W] | Pump 1 Efficiency E1 [%] | Pump 2 Efficiency E2 [%] | Overall Efficiency Egr [%] | Walkthrough Questions Score [%]
1 |  | 70 | 1260 | 30.45 | 2.5749 | 32.3882 | 109.812 | 0.32928 | 0 | Series | 995.5455 | 0 | 0 | 0 | 0 | 3.1277 | 7.9276 | 11.0553 | 0 | 0 | 0 | 43.447 | 0 | 0 | 0
2 |  | 70 | 1260 | 33.3 | 2.6254 | 32.3882 | 111.2762 | 0.32928 | 0 | Series | 994.6623 | 0 | 0 | 0 | 0 | 3.1252 | 8.0847 | 11.2099 | 0 | 0 | 0 | 43.447 | 0 | 0 | 0
3 |  | 70 | 1260 | 26.95 | 2.5749 | 31.3785 | 107.3886 | 0.31073 | 0.037109 | Series | 996.5311 | 0.085557 | 0.15428 | 0.15428 | 0.15428 | 3.0222 | 7.7752 | 10.7974 | 1.0964 | 2.8207 | 3.9171 | 40.9993 | 2.6742 | 6.8798 | 4.777
4 |  | 70 | 1260 | 30.5 | 2.4234 | 31.5047 | 106.2273 | 0.33546 | 0.056641 | Series | 995.5307 | 0.13059 | 0.23548 | 0.23548 | 0.23548 | 3.0547 | 7.6512 | 10.7059 | 1.6897 | 4.2323 | 5.9221 | 44.2629 | 3.8175 | 9.5618 | 6.6897
5 |  | 70 | 1260 | 27 | 2.4739 | 31.1513 | 104.3593 | 0.30918 | 0.076172 | Series | 996.5178 | 0.17562 | 0.31669 | 0.31669 | 0.31669 | 3.012 | 7.4887 | 10.5007 | 2.2429 | 5.5764 | 7.8193 | 40.7953 | 5.4979 | 13.6692 | 9.5836
6 |  | 70 | 1260 | 27 | 2.5244 | 30.4444 | 103.3495 | 0.31227 | 0.13281 | Series | 996.5178 | 0.30621 | 0.55217 | 0.55217 | 0.55217 | 2.9418 | 7.4577 | 10.3995 | 3.8195 | 9.6827 | 13.5022 | 41.2033 | 9.2698 | 23.4999 | 16.3848
7 |  | 70 | 1260 | 30.45 | 2.3225 | 30.5202 | 103.6524 | 0.3401 | 0.15039 | Series | 995.5455 | 0.34673 | 0.62525 | 0.62525 | 0.62525 | 2.976 | 7.4882 | 10.4643 | 4.3711 | 10.9984 | 15.3695 | 44.8748 | 9.7406 | 24.5091 | 17.1249
8 |  | 70 | 1260 | 26.95 | 2.4234 | 28.9045 | 99.3609 | 0.32464 | 0.20703 | Series | 996.5311 | 0.47732 | 0.86074 | 0.86074 | 0.86074 | 2.8099 | 7.2071 | 10.017 | 5.6871 | 14.5867 | 20.2738 | 42.8351 | 13.2768 | 34.0531 | 23.665
9 |  | 70 | 1260 | 27 | 2.4739 | 29.4599 | 102.2388 | 0.31691 | 0.20703 | Series | 996.5178 | 0.47732 | 0.86074 | 0.86074 | 0.86074 | 2.8616 | 7.4448 | 10.3064 | 5.7917 | 15.0675 | 20.8592 | 41.8152 | 13.8506 | 36.0336 | 24.9421
10 |  | 70 | 1260 | 33.25 | 2.5749 | 29.3842 | 101.8349 | 0.34319 | 0.22656 | Series | 994.6784 | 0.52235 | 0.94194 | 0.94194 | 0.94194 | 2.8538 | 7.4249 | 10.2787 | 6.309 | 16.4146 | 22.7236 | 45.2828 | 13.9325 | 36.2491 | 25.0908
11 |  | 70 | 1260 | 30.45 | 2.4234 | 29.258 | 101.4814 | 0.34783 | 0.2832 | Series | 995.5455 | 0.65294 | 1.1774 | 1.1774 | 1.1774 | 2.8716 | 7.3952 | 10.2668 | 7.9424 | 20.4539 | 28.3963 | 45.8947 | 17.3057 | 44.567 | 30.9364
12 |  | 70 | 1260 | 26.95 | 2.3729 | 27.1879 | 95.1704 | 0.32618 | 0.37695 | Series | 996.5311 | 0.86908 | 1.5672 | 1.5672 | 1.5672 | 2.7001 | 6.954 | 9.6541 | 9.9499 | 25.6262 | 35.5761 | 43.039 | 23.1183 | 59.5418 | 41.3301
13 |  | 70 | 1260 | 30.35 | 2.4234 | 27.2132 | 96.988 | 0.35092 | 0.37695 | Series | 995.5752 | 0.86908 | 1.5672 | 1.5672 | 1.5672 | 2.6999 | 7.1442 | 9.8441 | 9.9398 | 26.3018 | 36.2417 | 46.3027 | 21.4671 | 56.8041 | 39.1356
14 |  | 70 | 1260 | 27.1 | 2.4234 | 26.8093 | 95.4733 | 0.33237 | 0.39648 | Series | 996.4911 | 0.91411 | 1.6484 | 1.6484 | 1.6484 | 2.6655 | 7.024 | 9.6895 | 10.331 | 27.2242 | 37.5552 | 43.8549 | 23.5572 | 62.0779 | 42.8175
15 |  | 70 | 1260 | 33.25 | 2.4739 | 27.6423 | 96.3316 | 0.35092 | 0.39648 | Series | 994.6784 | 0.91411 | 1.6484 | 1.6484 | 1.6484 | 2.7502 | 7.0394 | 9.7896 | 10.6401 | 27.2342 | 37.8743 | 46.3027 | 22.9794 | 58.8179 | 40.8986
16 |  | 70 | 1260 | 27.2 | 2.3729 | 24.4616 | 90.5255 | 0.34474 | 0.43359 | Series | 996.4644 | 0.99967 | 1.8027 | 1.8027 | 1.8027 | 2.4493 | 6.7582 | 9.2076 | 10.3815 | 28.6449 | 39.0264 | 45.4868 | 22.8231 | 62.9742 | 42.8986
17 |  | 70 | 1260 | 30.4 | 2.3225 | 26.5821 | 94.817 | 0.3571 | 0.45312 | Series | 995.5604 | 1.0447 | 1.8839 | 1.8839 | 1.8839 | 2.6842 | 6.9867 | 9.6709 | 11.8789 | 30.9189 | 42.7978 | 47.1186 | 25.2106 | 65.6194 | 45.415
18 |  | 70 | 1260 | 30.4 | 2.272 | 25.1937 | 90.374 | 0.36019 | 0.52734 | Series | 995.5604 | 1.2158 | 2.1924 | 2.1924 | 2.1924 | 2.5916 | 6.6739 | 9.2655 | 13.3476 | 34.3725 | 47.7201 | 47.5265 | 28.0846 | 72.3227 | 50.2036
19 |  | 70 | 1260 | 33.2 | 2.2215 | 22.4168 | 86.1835 | 0.36638 | 0.60352 | Series | 994.6945 | 1.3914 | 2.5091 | 2.5091 | 2.5091 | 2.3668 | 6.5348 | 8.9017 | 13.9384 | 38.4842 | 52.4226 | 48.3424 | 28.8327 | 79.6075 | 54.2201
20 |  | 70 | 1260 | 30.35 | 2.272 | 22.4925 | 85.4262 | 0.36947 | 0.62305 | Series | 995.5752 | 1.4365 | 2.5903 | 2.5903 | 2.5903 | 2.3822 | 6.4438 | 8.826 | 14.4958 | 39.2106 | 53.7064 | 48.7504 | 29.7347 | 80.4314 | 55.083
21 |  | 70 | 1260 | 26.9 | 2.171 | 19.1855 | 76.8937 | 0.35092 | 0.73633 | Series | 996.5444 | 1.6976 | 3.0613 | 3.0613 | 3.0613 | 2.1462 | 5.903 | 8.0492 | 15.4491 | 42.4921 | 57.9412 | 46.3027 | 33.3655 | 91.7703 | 62.5679
22 |  | 70 | 1260 | 30.35 | 1.9186 | 16.8126 | 73.5109 | 0.38029 | 0.77344 | Series | 995.5752 | 1.7832 | 3.2156 | 3.2156 | 3.2156 | 1.9649 | 5.8053 | 7.7703 | 14.8429 | 43.8526 | 58.6955 | 50.1782 | 29.5803 | 87.3937 | 58.487
23 |  | 70 | 1260 | 26.9 | 2.07 | 15.3737 | 68.2602 | 0.35865 | 0.81055 | Series | 996.5444 | 1.8688 | 3.3699 | 3.3699 | 3.3699 | 1.8366 | 5.4098 | 7.2464 | 14.5535 | 42.867 | 57.4205 | 47.3225 | 30.7538 | 90.5847 | 60.6692
24 |  | 70 | 1260 | 33.2 | 1.8681 | 15.197 | 69.8253 | 0.38029 | 0.83008 | Series | 994.6945 | 1.9138 | 3.4511 | 3.4511 | 3.4511 | 1.8613 | 5.5983 | 7.4596 | 15.0763 | 45.3458 | 60.4221 | 50.1782 | 30.0455 | 90.3694 | 60.2075
25 |  | 70 | 1260 | 30.3 | 2.07 | 14.7931 | 66.9979 | 0.38493 | 0.86719 | Series | 995.59 | 1.9993 | 3.6053 | 3.6053 | 3.6053 | 1.8365 | 5.3452 | 7.1816 | 15.5541 | 45.2714 | 60.8255 | 50.7901 | 30.6243 | 89.1343 | 59.8793
26 |  | 70 | 1260 | 27.25 | 1.9186 | 13.4299 | 67.8563 | 0.36638 | 0.88672 | Series | 996.451 | 2.0444 | 3.6865 | 3.6865 | 3.6865 | 1.7323 | 5.5678 | 7.3001 | 15.0151 | 48.2609 | 63.276 | 48.3424 | 31.0599 | 99.8313 | 65.4456
27 |  | 70 | 1260 | 26.85 | 1.9186 | 12.6726 | 65.5843 | 0.36019 | 0.9043 | Series | 996.5576 | 2.0849 | 3.7596 | 3.7596 | 3.7596 | 1.6739 | 5.4123 | 7.0862 | 14.7983 | 47.8479 | 62.6462 | 47.5265 | 31.1368 | 100.6762 | 65.9065
28 |  | 70 | 1260 | 30.25 | 1.7671 | 9.2898 | 58.5664 | 0.3942 | 0.96094 | Series | 995.6048 | 2.2155 | 3.9951 | 3.9951 | 3.9951 | 1.4086 | 5.0453 | 6.4538 | 13.2199 | 47.3517 | 60.5716 | 52.014 | 25.416 | 91.0364 | 58.2262
29 |  | 70 | 1260 | 27.3 | 1.9186 | 9.2646 | 59.5762 | 0.37411 | 0.98047 | Series | 996.4375 | 2.2605 | 4.0763 | 4.0763 | 4.0763 | 1.413 | 5.1469 | 6.5599 | 13.5421 | 49.3289 | 62.871 | 49.3623 | 27.4341 | 99.9324 | 63.6832
30 |  | 70 | 1260 | 26.8 | 1.7671 | 7.9771 | 56.7993 | 0.36329 | 1 | Series | 996.5708 | 2.3055 | 4.1575 | 4.1575 | 4.1575 | 1.3203 | 4.9939 | 6.3142 | 12.9075 | 48.8222 | 61.7296 | 47.9345 | 26.9273 | 101.8519 | 64.3896
31 |  | 70 | 1260 | 33.15 | 1.6661 | 8.8102 | 58.011 | 0.3973 | 1.0176 | Series | 994.7105 | 2.3461 | 4.2306 | 4.2306 | 4.2306 | 1.4388 | 5.042 | 6.4809 | 14.2869 | 50.0657 | 64.3526 | 52.422 | 27.2537 | 95.5052 | 61.3794
32 |  | 70 | 1260 | 27.25 | 1.6661 | 5.4527 | 51.0437 | 0.38029 | 1.0566 | Series | 996.451 | 2.4361 | 4.393 | 4.393 | 4.393 | 1.1435 | 4.6639 | 5.8074 | 11.811 | 48.1732 | 59.9842 | 50.1782 | 23.5381 | 96.0042 | 59.7712
33 |  | 70 | 1260 | 26.7 | 1.6661 | 2.3477 | 45.086 | 0.37256 | 1.1133 | Series | 996.5972 | 2.5667 | 4.6285 | 4.6285 | 4.6285 | 0.90082 | 4.3715 | 5.2723 | 9.8047 | 47.5798 | 57.3844 | 49.1583 | 19.9451 | 96.7888 | 58.367
34 |  | 70 | 1260 | 30.1 | 1.6661 | 3.408 | 46.3482 | 0.39884 | 1.1133 | Series | 995.6491 | 2.5667 | 4.6285 | 4.6285 | 4.6285 | 1.0094 | 4.3963 | 5.4058 | 10.9764 | 47.8046 | 58.781 | 52.6259 | 20.8574 | 90.8385 | 55.848
35 |  | 70 | 1260 | 27.35 | 1.4137 | 0 | 40.6936 | 0.39266 | 1.1504 | Series | 996.4241 | 2.6523 | 4.7828 | 4.7828 | 4.7828 | 0.73773 | 4.1631 | 4.9008 | 8.2958 | 46.8135 | 55.1093 | 51.81 | 16.0119 | 90.356 | 53.184
36 |  | 70 | 1260 | 33.05 | 1.6661 | 0 | 39.6333 | 0.40657 | 1.1504 | Series | 994.7426 | 2.6523 | 4.7828 | 4.7828 | 4.7828 | 0.71162 | 4.0614 | 4.7731 | 7.9886 | 45.5938 | 53.5824 | 53.6458 | 14.8914 | 84.9904 | 49.9409
37 |  | 70 | 1260 | 27.35 | 1.5146 | 0 | 37.5633 | 0.39266 | 1.1699 | Series | 996.4241 | 2.6973 | 4.864 | 4.864 | 4.864 | 0.75505 | 3.8428 | 4.5979 | 8.6346 | 43.9461 | 52.5808 | 51.81 | 16.666 | 84.8216 | 50.7438
38 |  | 70 | 1260 | 26.65 | 1.3632 | 0 | 34.5845 | 0.37875 | 1.1875 | Series | 996.6104 | 2.7378 | 4.9371 | 4.9371 | 4.9371 | 0.79585 | 3.5374 | 4.3333 | 9.2397 | 41.0691 | 50.3088 | 49.9742 | 18.489 | 82.1805 | 50.3347
39 |  | 70 | 1260 | 30 | 1.5146 | 0 | 35.4933 | 0.40966 | 1.207 | Series | 995.6784 | 2.7829 | 5.0183 | 5.0183 | 5.0183 | 0.80874 | 3.6338 | 4.4425 | 9.5349 | 42.8415 | 52.3764 | 54.0538 | 17.6397 | 79.2571 | 48.4484
40 |  | 70 | 1260 | 27.35 | 1.4137 | 0 | 33.0193 | 0.40039 | 1.2266 | Series | 996.4241 | 2.8279 | 5.0995 | 5.0995 | 5.0995 | 0.84819 | 3.378 | 4.2262 | 10.1694 | 40.5003 | 50.6697 | 52.8299 | 19.2493 | 76.6616 | 47.9555
41 |  | 70 | 1260 | 27.4 | 1.4137 | 0 | 31.1513 | 0.3973 | 1.2266 | Series | 996.4106 | 2.8279 | 5.0995 | 5.0995 | 5.0995 | 0.84818 | 3.1869 | 4.0351 | 10.1692 | 38.209 | 48.3782 | 52.422 | 19.3988 | 72.8874 | 46.1431
42 |  | 70 | 1260 | 27.4 | 1.3632 | 0 | 29.6871 | 0.39884 | 1.2441 | Series | 996.4106 | 2.8684 | 5.1725 | 5.1725 | 5.1725 | 0.87985 | 3.0371 | 3.917 | 10.7 | 36.9349 | 47.6349 | 52.6259 | 20.3321 | 70.1839 | 45.258
43 |  | 70 | 1260 | 27.4 | 1.3127 | 0 | 28.5259 | 0.40193 | 1.2637 | Series | 996.4106 | 2.9135 | 5.2537 | 5.2537 | 5.2537 | 0.91489 | 2.9183 | 3.8332 | 11.3009 | 36.0474 | 47.3482 | 53.0339 | 21.3087 | 67.9704 | 44.6396
44 |  | 70 | 1260 | 32.9 | 1.2117 | 0 | 27.3142 | 0.4143 | 1.2637 | Series | 994.7905 | 2.9135 | 5.2537 | 5.2537 | 5.2537 | 0.92502 | 2.7989 | 3.7239 | 11.4074 | 34.5161 | 45.9235 | 54.6657 | 20.8675 | 63.1404 | 42.004
45 |  | 70 | 1260 | 26.4 | 1.2117 | 0 | 26.9607 | 0.3772 | 1.2832 | Series | 996.6758 | 2.9585 | 5.3349 | 5.3349 | 5.3349 | 0.9556 | 2.7575 | 3.7131 | 11.9893 | 34.5961 | 46.5854 | 49.7703 | 24.0894 | 69.5116 | 46.8005
46 |  | 70 | 1260 | 26.55 | 1.0603 | 0 | 26.7083 | 0.38029 | 1.2832 | Series | 996.6366 | 2.9585 | 5.3349 | 5.3349 | 5.3349 | 0.97109 | 2.7317 | 3.7028 | 12.1832 | 34.2722 | 46.4553 | 50.1782 | 24.2798 | 68.3009 | 46.2903
47 |  | 70 | 1260 | 26.65 | 1.2622 | 0 | 29.3337 | 0.38647 | 1.2832 | Series | 996.6104 | 2.9585 | 5.3349 | 5.3349 | 5.3349 | 0.95043 | 3.0004 | 3.9508 | 11.9237 | 37.6411 | 49.5647 | 50.9941 | 23.3824 | 73.8146 | 48.5985
48 |  | 70 | 1260 | 27.4 | 1.3127 | 0 | 28.2229 | 0.40503 | 1.2832 | Series | 996.4106 | 2.9585 | 5.3349 | 5.3349 | 5.3349 | 0.94524 | 2.8873 | 3.8326 | 11.8562 | 36.2158 | 48.0719 | 53.4418 | 22.1852 | 67.7667 | 44.9759
49 |  | 70 | 1260 | 27.45 | 1.1612 | 0 | 26.8093 | 0.40657 | 1.2832 | Series | 996.3971 | 2.9585 | 5.3349 | 5.3349 | 5.3349 | 0.96073 | 2.7427 | 3.7035 | 12.0503 | 34.4017 | 46.4521 | 53.6458 | 22.4628 | 64.1275 | 43.2952
50 |  | 70 | 1260 | 27.45 | 1.4137 | 0 | 25.3956 | 0.40503 | 1.2832 | Series | 996.3971 | 2.9585 | 5.3349 | 5.3349 | 5.3349 | 0.93491 | 2.5981 | 3.533 | 11.7264 | 32.5877 | 44.3141 | 53.4418 | 21.9424 | 60.9779 | 41.4601
51 |  | 70 | 1260 | 32.55 | 1.4137 | 0 | 25.1937 | 0.42512 | 1.2832 | Series | 994.9016 | 2.9585 | 5.3349 | 5.3349 | 5.3349 | 0.93469 | 2.5813 | 3.516 | 11.7061 | 32.3286 | 44.0347 | 56.0935 | 20.8689 | 57.6333 | 39.2511
52 |  | 70 | 1260 | 32.75 | 1.2622 | 0 | 25.6985 | 0.42512 | 1.2832 | Series | 994.8383 | 2.9585 | 5.3349 | 5.3349 | 5.3349 | 0.9502 | 2.6332 | 3.5834 | 11.8996 | 32.9764 | 44.876 | 56.0935 | 21.2138 | 58.7883 | 40.0011
53 |  | 70 | 1260 | 32.65 | 1.1612 | 0 | 25.951 | 0.40193 | 1.2832 | Series | 994.87 | 2.9585 | 5.3349 | 5.3349 | 5.3349 | 0.96055 | 2.659 | 3.6195 | 12.0296 | 33.3004 | 45.33 | 53.0339 | 22.6828 | 62.7907 | 42.7368
54 |  | 70 | 1260 | 26.55 | 1.2117 | 0 | 26.5063 | 0.38029 | 1.3008 | Series | 996.6366 | 2.999 | 5.408 | 5.408 | 5.408 | 0.98331 | 2.7111 | 3.6944 | 12.5054 | 34.479 | 46.9844 | 50.1782 | 24.9221 | 68.713 | 46.8175
55 |  | 70 | 1260 | 32.3 | 1.2117 | 0 | 26.7588 | 0.42048 | 1.3008 | Series | 994.9803 | 2.999 | 5.408 | 5.408 | 5.408 | 0.9831 | 2.7415 | 3.7246 | 12.482 | 34.8073 | 47.2894 | 55.4816 | 22.4976 | 62.7367 | 42.6172
56 |  | 70 | 1260 | 32.6 | 1.4642 | 0 | 27.0112 | 0.40348 | 1.3008 | Series | 994.8858 | 2.999 | 5.408 | 5.408 | 5.408 | 0.95722 | 2.7676 | 3.7248 | 12.1523 | 35.1357 | 47.288 | 53.2379 | 22.8265 | 65.9976 | 44.412
57 |  | 70 | 1260 | 33.35 | 0.40391 | 23.9567 | 34.534 | 0.36174 | 1.7539 | Series | 994.6462 | 4.0437 | 7.2919 | 7.2919 | 7.2919 | 4.3655 | 1.084 | 5.4495 | 74.7095 | 18.5516 | 93.2611 | 47.7305 | 156.5236 | 38.8674 | 97.6955

## Parallel
Sample Number | Notes | Pump Setting S [%] | Pump Speed n [rpm] | Water Temperature T [°C] | Inlet Pressure P0 [kPa] | Pump 1 Pressure P1 [kPa] | Pump 2 Pressure P2 [kPa] | Motor 1 Torque t [Nm] | Flow Rate Q [l/s] | Operating Mode | Density of water rho [kg/m³] | Pump 1 Inlet Velocity [m/s] | Pump 1 Outlet Velocity [m/s] | Pump 2 Inlet Velocity [m/s] | Pump 2 Outlet Velocity [m/s] | Pump 1 Total Head [m] | Pump 2 Total Head [m] | Combined Total Head [m] | Pump 1 Hydraulic Power [W] | Pump 2 Hydraulic Power [W] | Total Hydraulic Power [W] | Pump 1 Mechanical Power [W] | Pump 1 Efficiency E1 [%] | Pump 2 Efficiency E2 [%] | Overall Efficiency Egr [%] | Walkthrough Questions Score [%]
1 |  | 70 | 1260 | 28.25 | 2.5244 | 55.3856 | 66.8465 | 0.34628 | 0 | Parallel | 996.178 | 0 | 0 | 0 | 0 | 5.4842 | 6.6569 | 6.0706 | 0 | 0 | 0 | 45.6907 | 0 | 0 | 0
2 |  | 70 | 1260 | 28.25 | 2.5244 | 55.3856 | 66.8465 | 0.34628 | 0 | Parallel | 996.178 | 0 | 0 | 0 | 0 | 5.4842 | 6.6569 | 6.0706 | 0 | 0 | 0 | 45.6907 | 0 | 0 | 0
3 |  | 70 | 1260 | 29.25 | 2.5244 | 55.6633 | 68.2602 | 0.34783 | 0 | Parallel | 995.8959 | 0 | 0 | 0 | 0 | 5.5141 | 6.8035 | 6.1588 | 0 | 0 | 0 | 45.8947 | 0 | 0 | 0
4 |  | 70 | 1260 | 29.25 | 2.4234 | 57.2285 | 67.0989 | 0.34783 | 0 | Parallel | 995.8959 | 0 | 0 | 0 | 0 | 5.6847 | 6.695 | 6.1898 | 0 | 0 | 0 | 45.8947 | 0 | 0 | 0
5 |  | 70 | 1260 | 31.35 | 2.4234 | 55.4866 | 66.6445 | 0.35865 | 0 | Parallel | 995.2743 | 0 | 0 | 0 | 0 | 5.5098 | 6.6526 | 6.0812 | 0 | 0 | 0 | 47.3225 | 0 | 0 | 0
6 |  | 70 | 1260 | 33.75 | 2.5749 | 57.1275 | 67.7553 | 0.36019 | 0 | Parallel | 994.5164 | 0 | 0 | 0 | 0 | 5.6666 | 6.7559 | 6.2112 | 0 | 0 | 0 | 47.5265 | 0 | 0 | 0
7 |  | 70 | 1260 | 29.3 | 2.4739 | 56.1682 | 65.8367 | 0.34937 | 0.019531 | Parallel | 995.8816 | 0.022515 | 0.040601 | 0.022515 | 0.040601 | 5.5711 | 6.5608 | 6.0659 | 0.53152 | 0.62594 | 1.1575 | 46.0987 | 1.153 | 1.3578 | 1.2554
8 |  | 70 | 1260 | 31.4 | 2.4739 | 56.1177 | 67.3514 | 0.36019 | 0.037109 | Parallel | 995.259 | 0.042779 | 0.077141 | 0.042779 | 0.077141 | 5.5695 | 6.7201 | 6.1448 | 1.009 | 1.2174 | 2.2264 | 47.5265 | 2.123 | 2.5615 | 2.3422
9 |  | 70 | 1260 | 29.25 | 2.4739 | 56.0167 | 66.0387 | 0.34319 | 0.056641 | Parallel | 995.8959 | 0.065294 | 0.11774 | 0.065294 | 0.11774 | 5.556 | 6.5818 | 6.0689 | 1.5372 | 1.8211 | 3.3583 | 45.2828 | 3.3947 | 4.0215 | 3.7081
10 |  | 70 | 1260 | 31.35 | 2.5244 | 54.4011 | 67.0989 | 0.35556 | 0.056641 | Parallel | 995.2743 | 0.065294 | 0.11774 | 0.065294 | 0.11774 | 5.3887 | 6.6893 | 6.039 | 1.49 | 1.8496 | 3.3397 | 46.9146 | 3.1761 | 3.9426 | 3.5593
11 |  | 70 | 1260 | 29.2 | 2.4234 | 54.7293 | 65.8872 | 0.34164 | 0.09375 | Parallel | 995.9102 | 0.10807 | 0.19488 | 0.10807 | 0.19488 | 5.4301 | 6.5722 | 6.0012 | 2.4868 | 3.0098 | 5.4966 | 45.0788 | 5.5166 | 6.6768 | 6.0967
12 |  | 70 | 1260 | 28.25 | 2.4234 | 55.4109 | 65.4328 | 0.34783 | 0.11328 | Parallel | 996.178 | 0.13059 | 0.23548 | 0.13059 | 0.23548 | 5.4991 | 6.5246 | 6.0118 | 3.0438 | 3.6115 | 6.6553 | 45.8947 | 6.6322 | 7.8691 | 7.2506
13 |  | 70 | 1260 | 28.25 | 2.4234 | 55.4109 | 65.4328 | 0.34783 | 0.11328 | Parallel | 996.178 | 0.13059 | 0.23548 | 0.13059 | 0.23548 | 5.4991 | 6.5246 | 6.0118 | 3.0438 | 3.6115 | 6.6553 | 45.8947 | 6.6322 | 7.8691 | 7.2506
14 |  | 70 | 1260 | 31.3 | 2.4739 | 55.1584 | 65.8872 | 0.35401 | 0.11328 | Parallel | 995.2896 | 0.13059 | 0.23548 | 0.13059 | 0.23548 | 5.4729 | 6.5717 | 6.0223 | 3.0266 | 3.6343 | 6.661 | 46.7106 | 6.4796 | 7.7805 | 7.13
15 |  | 70 | 1260 | 31.35 | 2.4234 | 55.3352 | 65.8367 | 0.35556 | 0.15039 | Parallel | 995.2743 | 0.17337 | 0.31263 | 0.17337 | 0.31263 | 5.4977 | 6.5733 | 6.0355 | 4.0363 | 4.826 | 8.8623 | 46.9146 | 8.6035 | 10.2867 | 9.4451
16 |  | 70 | 1260 | 29.25 | 2.3729 | 53.4418 | 63.9687 | 0.34164 | 0.16992 | Parallel | 995.8959 | 0.19588 | 0.35323 | 0.19588 | 0.35323 | 5.3067 | 6.3841 | 5.8454 | 4.4048 | 5.2991 | 9.7039 | 45.0788 | 9.7713 | 11.7553 | 10.7633
17 |  | 70 | 1260 | 28.3 | 2.4234 | 55.3099 | 64.2716 | 0.34628 | 0.18945 | Parallel | 996.1641 | 0.2184 | 0.39383 | 0.2184 | 0.39383 | 5.4923 | 6.4094 | 5.9508 | 5.0842 | 5.9332 | 11.0174 | 45.6907 | 11.1275 | 12.9855 | 12.0565
18 |  | 70 | 1260 | 28.3 | 2.4234 | 55.3099 | 64.2716 | 0.34628 | 0.18945 | Parallel | 996.1641 | 0.2184 | 0.39383 | 0.2184 | 0.39383 | 5.4923 | 6.4094 | 5.9508 | 5.0842 | 5.9332 | 11.0174 | 45.6907 | 11.1275 | 12.9855 | 12.0565
19 |  | 70 | 1260 | 31.3 | 2.4234 | 54.805 | 64.4735 | 0.35401 | 0.18945 | Parallel | 995.2896 | 0.2184 | 0.39383 | 0.2184 | 0.39383 | 5.4454 | 6.4356 | 5.9405 | 5.0364 | 5.9522 | 10.9886 | 46.7106 | 10.782 | 12.7428 | 11.7624
20 |  | 70 | 1260 | 28.25 | 2.4234 | 53.9467 | 62.8579 | 0.34628 | 0.20703 | Parallel | 996.178 | 0.23866 | 0.43037 | 0.23866 | 0.43037 | 5.3538 | 6.2657 | 5.8097 | 5.4159 | 6.3384 | 11.7543 | 45.6907 | 11.8535 | 13.8724 | 12.8629
21 |  | 70 | 1260 | 28.25 | 2.4234 | 53.9467 | 62.8579 | 0.34628 | 0.20703 | Parallel | 996.178 | 0.23866 | 0.43037 | 0.23866 | 0.43037 | 5.3538 | 6.2657 | 5.8097 | 5.4159 | 6.3384 | 11.7543 | 45.6907 | 11.8535 | 13.8724 | 12.8629
22 |  | 70 | 1260 | 31.3 | 2.4739 | 53.1389 | 63.2618 | 0.35092 | 0.24609 | Parallel | 995.2896 | 0.28369 | 0.51157 | 0.28369 | 0.51157 | 5.2733 | 6.3101 | 5.7917 | 6.3354 | 7.581 | 13.9163 | 46.3027 | 13.6825 | 16.3726 | 15.0276
23 |  | 70 | 1260 | 29.25 | 2.4739 | 52.8107 | 61.5957 | 0.33855 | 0.26367 | Parallel | 995.8959 | 0.30395 | 0.54811 | 0.30395 | 0.54811 | 5.2379 | 6.1371 | 5.6875 | 6.7465 | 7.9046 | 14.6511 | 44.6709 | 15.1026 | 17.6953 | 16.3989
24 |  | 70 | 1260 | 33.75 | 2.4739 | 54.3254 | 64.2211 | 0.34783 | 0.26367 | Parallel | 994.5164 | 0.30395 | 0.54811 | 0.30395 | 0.54811 | 5.4003 | 6.4146 | 5.9075 | 6.946 | 8.2506 | 15.1966 | 45.8947 | 15.1346 | 17.9772 | 16.5559
25 |  | 70 | 1260 | 31.25 | 2.4234 | 52.2806 | 61.4442 | 0.35246 | 0.30078 | Parallel | 995.3048 | 0.34673 | 0.62525 | 0.34673 | 0.62525 | 5.1951 | 6.1336 | 5.6643 | 7.6284 | 9.0066 | 16.635 | 46.5066 | 16.4029 | 19.3662 | 17.8846
1 |  | 70 | 1260 | 29.35 | 2.3729 | 52.3311 | 60.6869 | 0.33855 | 0.33984 | Parallel | 995.8672 | 0.39176 | 0.70645 | 0.39176 | 0.70645 | 5.2063 | 6.0616 | 5.634 | 8.6427 | 10.0626 | 18.7053 | 44.6709 | 19.3476 | 22.526 | 20.9368
2 |  | 70 | 1260 | 28.3 | 2.4234 | 50.766 | 60.283 | 0.3401 | 0.37695 | Parallel | 996.1641 | 0.43454 | 0.78359 | 0.43454 | 0.78359 | 5.0435 | 6.0174 | 5.5305 | 9.2895 | 11.0832 | 20.3727 | 44.8748 | 20.7009 | 24.6981 | 22.6995
3 |  | 70 | 1260 | 28.3 | 2.4234 | 50.766 | 60.283 | 0.3401 | 0.37695 | Parallel | 996.1641 | 0.43454 | 0.78359 | 0.43454 | 0.78359 | 5.0435 | 6.0174 | 5.5305 | 9.2895 | 11.0832 | 20.3727 | 44.8748 | 20.7009 | 24.6981 | 22.6995
4 |  | 70 | 1260 | 28.25 | 2.3225 | 52.1796 | 60.9394 | 0.34164 | 0.39648 | Parallel | 996.178 | 0.45706 | 0.8242 | 0.45706 | 0.8242 | 5.2008 | 6.0971 | 5.6489 | 10.0755 | 11.8121 | 21.8876 | 45.0788 | 22.351 | 26.2032 | 24.2771
5 |  | 70 | 1260 | 28.25 | 2.3225 | 52.1796 | 60.9394 | 0.34164 | 0.39648 | Parallel | 996.178 | 0.45706 | 0.8242 | 0.45706 | 0.8242 | 5.2008 | 6.0971 | 5.6489 | 10.0755 | 11.8121 | 21.8876 | 45.0788 | 22.351 | 26.2032 | 24.2771
6 |  | 70 | 1260 | 31.3 | 2.3225 | 51.6243 | 60.3335 | 0.34628 | 0.41406 | Parallel | 995.2896 | 0.47732 | 0.86074 | 0.47732 | 0.86074 | 5.1506 | 6.0426 | 5.5966 | 10.4115 | 12.2146 | 22.626 | 45.6907 | 22.7868 | 26.7331 | 24.76
7 |  | 70 | 1260 | 33.75 | 2.3729 | 49.9329 | 59.8791 | 0.34783 | 0.45312 | Parallel | 994.5164 | 0.52235 | 0.94194 | 0.52235 | 0.94194 | 4.9812 | 6.0006 | 5.4909 | 11.0103 | 13.2637 | 24.274 | 45.8947 | 23.9903 | 28.9004 | 26.4454
8 |  | 70 | 1260 | 31.3 | 2.3729 | 49.2008 | 57.9605 | 0.33855 | 0.4707 | Parallel | 995.2896 | 0.54261 | 0.97848 | 0.54261 | 0.97848 | 4.9049 | 5.802 | 5.3534 | 11.271 | 13.3326 | 24.6036 | 44.6709 | 25.2312 | 29.8464 | 27.5388
9 |  | 70 | 1260 | 29.4 | 2.2215 | 47.9891 | 56.0925 | 0.32773 | 0.54688 | Parallel | 995.8528 | 0.63042 | 1.1368 | 0.63042 | 1.1368 | 4.8054 | 5.6349 | 5.2202 | 12.8368 | 15.0525 | 27.8893 | 43.243 | 29.6852 | 34.8092 | 32.2472
10 |  | 70 | 1260 | 29.2 | 2.272 | 47.8124 | 55.84 | 0.33391 | 0.56641 | Parallel | 995.9102 | 0.65294 | 1.1774 | 0.65294 | 1.1774 | 4.7852 | 5.6069 | 5.1961 | 13.2401 | 15.5135 | 28.7536 | 44.0589 | 30.0509 | 35.2109 | 32.6309
11 |  | 70 | 1260 | 31.25 | 2.272 | 48.1406 | 56.9508 | 0.34783 | 0.58398 | Parallel | 995.3048 | 0.6732 | 1.214 | 0.6732 | 1.214 | 4.8248 | 5.7271 | 5.2759 | 13.7554 | 16.3279 | 30.0833 | 45.8947 | 29.9716 | 35.5769 | 32.7742
12 |  | 70 | 1260 | 31.2 | 2.2215 | 47.7114 | 56.3449 | 0.34474 | 0.62305 | Parallel | 995.32 | 0.71823 | 1.2952 | 0.71823 | 1.2952 | 4.7931 | 5.6773 | 5.2352 | 14.5794 | 17.2689 | 31.8483 | 45.4868 | 32.052 | 37.9648 | 35.0084
13 |  | 70 | 1260 | 28.2 | 2.1205 | 46.1463 | 54.3254 | 0.32618 | 0.64062 | Parallel | 996.1919 | 0.7385 | 1.3317 | 0.7385 | 1.3317 | 4.6426 | 5.4795 | 5.0611 | 14.5327 | 17.1526 | 31.6853 | 43.039 | 33.7664 | 39.8535 | 36.8099
14 |  | 70 | 1260 | 28.2 | 2.1205 | 46.1463 | 54.3254 | 0.32618 | 0.64062 | Parallel | 996.1919 | 0.7385 | 1.3317 | 0.7385 | 1.3317 | 4.6426 | 5.4795 | 5.0611 | 14.5327 | 17.1526 | 31.6853 | 43.039 | 33.7664 | 39.8535 | 36.8099
15 |  | 70 | 1260 | 33.75 | 2.3225 | 45.9948 | 55.4866 | 0.33546 | 0.66016 | Parallel | 994.5164 | 0.76101 | 1.3723 | 0.76101 | 1.3723 | 4.6178 | 5.5907 | 5.1043 | 14.8709 | 18.0039 | 32.8748 | 44.2629 | 33.5967 | 40.6749 | 37.1358
16 |  | 70 | 1260 | 31.2 | 2.2215 | 44.9093 | 54.2244 | 0.33855 | 0.67969 | Parallel | 995.32 | 0.78353 | 1.4129 | 0.78353 | 1.4129 | 4.5174 | 5.4714 | 4.9944 | 14.9899 | 18.1555 | 33.1454 | 44.6709 | 33.5563 | 40.6429 | 37.0996
17 |  | 70 | 1260 | 28.4 | 2.171 | 44.2782 | 52.4068 | 0.32773 | 0.69727 | Parallel | 996.1363 | 0.80379 | 1.4494 | 0.80379 | 1.4494 | 4.4581 | 5.2899 | 4.874 | 15.1881 | 18.022 | 33.2101 | 43.243 | 35.1227 | 41.6761 | 38.3994
18 |  | 70 | 1260 | 28.4 | 2.171 | 44.2782 | 52.4068 | 0.32773 | 0.69727 | Parallel | 996.1363 | 0.80379 | 1.4494 | 0.80379 | 1.4494 | 4.4581 | 5.2899 | 4.874 | 15.1881 | 18.022 | 33.2101 | 43.243 | 35.1227 | 41.6761 | 38.3994
19 |  | 70 | 1260 | 31.2 | 2.1205 | 43.3442 | 51.9524 | 0.33546 | 0.75391 | Parallel | 995.32 | 0.86908 | 1.5672 | 0.86908 | 1.5672 | 4.3837 | 5.2653 | 4.8245 | 16.1345 | 19.3794 | 35.5139 | 44.2629 | 36.4515 | 43.7825 | 40.117
20 |  | 70 | 1260 | 29.45 | 2.07 | 42.5364 | 50.6902 | 0.32309 | 0.77344 | Parallel | 995.8384 | 0.8916 | 1.6078 | 0.8916 | 1.6078 | 4.3085 | 5.1431 | 4.7258 | 16.2771 | 19.4304 | 35.7075 | 42.6311 | 38.1813 | 45.5779 | 41.8796
21 |  | 70 | 1260 | 29.25 | 2.0195 | 40.4664 | 49.1756 | 0.32 | 0.81055 | Parallel | 995.8959 | 0.93438 | 1.6849 | 0.93438 | 1.6849 | 4.1105 | 5.0019 | 4.5562 | 16.2752 | 19.8048 | 36.08 | 42.2231 | 38.5456 | 46.9051 | 42.7253
22 |  | 70 | 1260 | 31.15 | 1.9186 | 40.3654 | 49.0746 | 0.33701 | 0.83008 | Parallel | 995.3352 | 0.95689 | 1.7255 | 0.95689 | 1.7255 | 4.1176 | 5.0096 | 4.5636 | 16.6867 | 20.3014 | 36.9882 | 44.4669 | 37.5262 | 45.6551 | 41.5907
23 |  | 70 | 1260 | 28.4 | 1.9186 | 39.3556 | 48.6707 | 0.32464 | 0.84961 | Parallel | 996.1363 | 0.97941 | 1.7661 | 0.97941 | 1.7661 | 4.0161 | 4.9693 | 4.4927 | 16.6718 | 20.6289 | 37.3007 | 42.8351 | 38.9209 | 48.1589 | 43.5399
24 |  | 70 | 1260 | 28.4 | 1.9186 | 39.3556 | 48.6707 | 0.32464 | 0.84961 | Parallel | 996.1363 | 0.97941 | 1.7661 | 0.97941 | 1.7661 | 4.0161 | 4.9693 | 4.4927 | 16.6718 | 20.6289 | 37.3007 | 42.8351 | 38.9209 | 48.1589 | 43.5399
25 |  | 70 | 1260 | 33.7 | 2.0195 | 39.2294 | 48.8727 | 0.33237 | 0.88672 | Parallel | 994.5327 | 1.0222 | 1.8433 | 1.0222 | 1.8433 | 4.0088 | 4.9972 | 4.503 | 17.3405 | 21.6159 | 38.9564 | 43.8549 | 39.5405 | 49.2895 | 44.415
26 |  | 70 | 1260 | 31.15 | 1.7671 | 37.538 | 46.9036 | 0.33082 | 0.92383 | Parallel | 995.3352 | 1.065 | 1.9204 | 1.065 | 1.9204 | 3.8686 | 4.8278 | 4.3482 | 17.4484 | 21.7745 | 39.223 | 43.651 | 39.9726 | 49.8833 | 44.928
27 |  | 70 | 1260 | 28.2 | 1.9186 | 36.7807 | 46.8531 | 0.32155 | 0.94336 | Parallel | 996.1919 | 1.0875 | 1.961 | 1.0875 | 1.961 | 3.778 | 4.8087 | 4.2934 | 17.4151 | 22.1661 | 39.5812 | 42.4271 | 41.0472 | 52.2451 | 46.6461
28 |  | 70 | 1260 | 28.2 | 1.9186 | 36.7807 | 46.8531 | 0.32155 | 0.94336 | Parallel | 996.1919 | 1.0875 | 1.961 | 1.0875 | 1.961 | 3.778 | 4.8087 | 4.2934 | 17.4151 | 22.1661 | 39.5812 | 42.4271 | 41.0472 | 52.2451 | 46.6461
29 |  | 70 | 1260 | 29.2 | 1.9186 | 36.4021 | 45.7929 | 0.32155 | 0.98047 | Parallel | 995.9102 | 1.1303 | 2.0382 | 1.1303 | 2.0382 | 3.7512 | 4.7124 | 4.2318 | 17.9664 | 22.5701 | 40.5366 | 42.4271 | 42.3466 | 53.1974 | 47.772
30 |  | 70 | 1260 | 31.15 | 1.7671 | 35.2661 | 45.7424 | 0.33391 | 1 | Parallel | 995.3352 | 1.1528 | 2.0788 | 1.1528 | 2.0788 | 3.6583 | 4.7312 | 4.1948 | 17.8602 | 23.0984 | 40.9586 | 44.0589 | 40.5372 | 52.4262 | 46.4817
31 |  | 70 | 1260 | 29.5 | 1.5146 | 32.5145 | 42.6626 | 0.32 | 1.0371 | Parallel | 995.824 | 1.1956 | 2.1559 | 1.1956 | 2.1559 | 3.4123 | 4.4511 | 3.9317 | 17.286 | 22.5484 | 39.8345 | 42.2231 | 40.9397 | 53.403 | 47.1714
32 |  | 70 | 1260 | 33.65 | 1.7166 | 32.7417 | 43.8238 | 0.33237 | 1.0938 | Parallel | 994.5489 | 1.2608 | 2.2736 | 1.2608 | 2.2736 | 3.4374 | 4.5733 | 4.0053 | 18.3405 | 24.4011 | 42.7415 | 43.8549 | 41.8208 | 55.6404 | 48.7306
33 |  | 70 | 1260 | 31.1 | 1.5651 | 32.0853 | 43.016 | 0.33701 | 1.1133 | Parallel | 995.3504 | 1.2834 | 2.3142 | 1.2834 | 2.3142 | 3.3897 | 4.5091 | 3.9494 | 18.4238 | 24.5083 | 42.9321 | 44.4669 | 41.4327 | 55.1158 | 48.2743
34 |  | 70 | 1260 | 28.55 | 1.5146 | 30.7221 | 41.5014 | 0.32309 | 1.1309 | Parallel | 996.0943 | 1.3036 | 2.3508 | 1.3036 | 2.3508 | 3.259 | 4.3621 | 3.8106 | 18.0068 | 24.1017 | 42.1085 | 42.6311 | 42.2387 | 56.5355 | 49.3871
35 |  | 70 | 1260 | 28.55 | 1.5146 | 30.7221 | 41.5014 | 0.32309 | 1.1309 | Parallel | 996.0943 | 1.3036 | 2.3508 | 1.3036 | 2.3508 | 3.259 | 4.3621 | 3.8106 | 18.0068 | 24.1017 | 42.1085 | 42.6311 | 42.2387 | 56.5355 | 49.3871
36 |  | 70 | 1260 | 29.5 | 1.4642 | 29.9396 | 40.6936 | 0.32464 | 1.1699 | Parallel | 995.824 | 1.3487 | 2.432 | 1.3487 | 2.432 | 3.1986 | 4.2994 | 3.749 | 18.2785 | 24.5692 | 42.8476 | 42.8351 | 42.6718 | 57.3576 | 50.0147
37 |  | 70 | 1260 | 28.2 | 1.5146 | 30.9493 | 41.4509 | 0.32773 | 1.1875 | Parallel | 996.1919 | 1.3689 | 2.4685 | 1.3689 | 2.4685 | 3.302 | 4.3766 | 3.8393 | 19.16 | 25.3953 | 44.5552 | 43.243 | 44.3077 | 58.7269 | 51.5173
38 |  | 70 | 1260 | 28.2 | 1.5146 | 30.9493 | 41.4509 | 0.32773 | 1.1875 | Parallel | 996.1919 | 1.3689 | 2.4685 | 1.3689 | 2.4685 | 3.302 | 4.3766 | 3.8393 | 19.16 | 25.3953 | 44.5552 | 43.243 | 44.3077 | 58.7269 | 51.5173
39 |  | 70 | 1260 | 29.2 | 1.4137 | 30.0153 | 39.8353 | 0.32309 | 1.2266 | Parallel | 995.9102 | 1.414 | 2.5497 | 1.414 | 2.5497 | 3.232 | 4.2371 | 3.7345 | 19.365 | 25.3874 | 44.7524 | 42.6311 | 45.4246 | 59.5514 | 52.488
40 |  | 70 | 1260 | 29.5 | 1.0098 | 28.6269 | 39.5828 | 0.32773 | 1.2441 | Parallel | 995.824 | 1.4342 | 2.5863 | 1.4342 | 2.5863 | 3.1381 | 4.2596 | 3.6988 | 19.0702 | 25.8856 | 44.9558 | 43.243 | 44.1 | 59.8607 | 51.9804
41 |  | 70 | 1260 | 31.05 | 1.3127 | 30.7726 | 41.5014 | 0.3401 | 1.2441 | Parallel | 995.3655 | 1.4342 | 2.5863 | 1.4342 | 2.5863 | 3.3281 | 4.4269 | 3.8775 | 20.2157 | 26.8897 | 47.1054 | 44.8748 | 45.049 | 59.9216 | 52.4853
42 |  | 70 | 1260 | 28.55 | 1.4137 | 30.1667 | 41.1984 | 0.33082 | 1.2637 | Parallel | 996.0943 | 1.4567 | 2.6269 | 1.4567 | 2.6269 | 3.261 | 4.39 | 3.8255 | 20.134 | 27.1042 | 47.2381 | 43.651 | 46.1249 | 62.093 | 54.1089
43 |  | 70 | 1260 | 28.55 | 1.4137 | 30.1667 | 41.1984 | 0.33082 | 1.2637 | Parallel | 996.0943 | 1.4567 | 2.6269 | 1.4567 | 2.6269 | 3.261 | 4.39 | 3.8255 | 20.134 | 27.1042 | 47.2381 | 43.651 | 46.1249 | 62.093 | 54.1089
44 |  | 70 | 1260 | 28.55 | 1.1612 | 29.3337 | 39.8353 | 0.32928 | 1.3203 | Parallel | 996.0943 | 1.522 | 2.7446 | 1.522 | 2.7446 | 3.2239 | 4.2986 | 3.7613 | 20.7971 | 27.7298 | 48.5269 | 43.447 | 47.8678 | 63.8244 | 55.8461
45 |  | 70 | 1260 | 28.55 | 1.1612 | 29.3337 | 39.8353 | 0.32928 | 1.3203 | Parallel | 996.0943 | 1.522 | 2.7446 | 1.522 | 2.7446 | 3.2239 | 4.2986 | 3.7613 | 20.7971 | 27.7298 | 48.5269 | 43.447 | 47.8678 | 63.8244 | 55.8461
46 |  | 70 | 1260 | 33.6 | 1.2117 | 29.5356 | 40.1382 | 0.34164 | 1.3203 | Parallel | 994.5652 | 1.522 | 2.7446 | 1.522 | 2.7446 | 3.2439 | 4.3306 | 3.7872 | 20.8937 | 27.8931 | 48.7868 | 45.0788 | 46.3493 | 61.8762 | 54.1128
47 |  | 70 | 1260 | 31.05 | 1.1612 | 28.1977 | 40.1382 | 0.34319 | 1.3398 | Parallel | 995.3655 | 1.5445 | 2.7852 | 1.5445 | 2.7852 | 3.1176 | 4.3405 | 3.7291 | 20.3939 | 28.3931 | 48.7871 | 45.2828 | 45.0369 | 62.7018 | 53.8693
48 |  | 70 | 1260 | 28.15 | 1.1612 | 28.955 | 39.0274 | 0.33546 | 1.3574 | Parallel | 996.2057 | 1.5648 | 2.8218 | 1.5648 | 2.8218 | 3.2 | 4.2307 | 3.7154 | 21.2254 | 28.0617 | 49.2871 | 44.2629 | 47.9531 | 63.3977 | 55.6754
49 |  | 70 | 1260 | 28.15 | 1.1612 | 28.955 | 39.0274 | 0.33546 | 1.3574 | Parallel | 996.2057 | 1.5648 | 2.8218 | 1.5648 | 2.8218 | 3.2 | 4.2307 | 3.7154 | 21.2254 | 28.0617 | 49.2871 | 44.2629 | 47.9531 | 63.3977 | 55.6754
50 |  | 70 | 1260 | 29.55 | 1.0603 | 28.122 | 39.3809 | 0.33546 | 1.377 | Parallel | 995.8095 | 1.5873 | 2.8624 | 1.5873 | 2.8624 | 3.1344 | 4.2869 | 3.7106 | 21.0806 | 28.8321 | 49.9127 | 44.2629 | 47.626 | 65.1383 | 56.3821
51 |  | 70 | 1260 | 29.2 | 1.0098 | 28.8288 | 40.0372 | 0.33082 | 1.3965 | Parallel | 995.9102 | 1.6098 | 2.903 | 1.6098 | 2.903 | 3.2199 | 4.3671 | 3.7935 | 21.9651 | 29.7912 | 51.7563 | 43.651 | 50.3197 | 68.2487 | 59.2842
52 |  | 70 | 1260 | 28.6 | 1.0603 | 27.7938 | 39.5828 | 0.33546 | 1.4141 | Parallel | 996.0803 | 1.6301 | 2.9395 | 1.6301 | 2.9395 | 3.1158 | 4.3223 | 3.7191 | 21.5266 | 29.8618 | 51.3883 | 44.2629 | 48.6334 | 67.4645 | 58.049
53 |  | 70 | 1260 | 28.6 | 1.0603 | 27.7938 | 39.5828 | 0.33546 | 1.4141 | Parallel | 996.0803 | 1.6301 | 2.9395 | 1.6301 | 2.9395 | 3.1158 | 4.3223 | 3.7191 | 21.5266 | 29.8618 | 51.3883 | 44.2629 | 48.6334 | 67.4645 | 58.049
54 |  | 70 | 1260 | 31.05 | 1.0098 | 27.819 | 39.2799 | 0.34628 | 1.4512 | Parallel | 995.3655 | 1.6729 | 3.0166 | 1.6729 | 3.0166 | 3.1418 | 4.3155 | 3.7286 | 22.2594 | 30.5752 | 52.8346 | 45.6907 | 48.7175 | 66.9177 | 57.8176
55 |  | 70 | 1260 | 28.6 | 0.8583 | 27.7181 | 38.0177 | 0.33855 | 1.4707 | Parallel | 996.0803 | 1.6954 | 3.0572 | 1.6954 | 3.0572 | 3.1537 | 4.2077 | 3.6807 | 22.6607 | 30.2345 | 52.8952 | 44.6709 | 50.7281 | 67.6829 | 59.2055
56 |  | 70 | 1260 | 28.6 | 0.8583 | 27.7181 | 38.0177 | 0.33855 | 1.4707 | Parallel | 996.0803 | 1.6954 | 3.0572 | 1.6954 | 3.0572 | 3.1537 | 4.2077 | 3.6807 | 22.6607 | 30.2345 | 52.8952 | 44.6709 | 50.7281 | 67.6829 | 59.2055
1 |  | 70 | 1260 | 29.1 | 0.80781 | 27.0112 | 37.6643 | 0.33546 | 1.4707 | Parallel | 995.9388 | 1.6954 | 3.0572 | 1.6954 | 3.0572 | 3.0869 | 4.1772 | 3.6321 | 22.1776 | 30.0113 | 52.189 | 44.2629 | 50.1043 | 67.8025 | 58.9534
2 |  | 70 | 1260 | 31 | 0.8583 | 27.3899 | 38.5226 | 0.35246 | 1.4902 | Parallel | 995.3806 | 1.7179 | 3.0978 | 1.7179 | 3.0978 | 3.1308 | 4.2709 | 3.7008 | 22.7792 | 31.0743 | 53.8535 | 46.5066 | 48.9805 | 66.817 | 57.8988
3 |  | 70 | 1260 | 29.55 | 0.80781 | 26.2034 | 38.2701 | 0.34319 | 1.5078 | Parallel | 995.8095 | 1.7382 | 3.1344 | 1.7382 | 3.1344 | 3.0214 | 4.2566 | 3.639 | 22.252 | 31.3491 | 53.6011 | 45.2828 | 49.14 | 69.2297 | 59.1849
4 |  | 70 | 1260 | 33.55 | 0.95928 | 27.9453 | 38.2701 | 0.34783 | 1.5078 | Parallel | 994.5814 | 1.7382 | 3.1344 | 1.7382 | 3.1344 | 3.1876 | 4.2458 | 3.7167 | 23.4471 | 31.2311 | 54.6782 | 45.8947 | 51.089 | 68.0495 | 59.5692
5 |  | 70 | 1260 | 28.6 | 0.65635 | 26.5316 | 37.4623 | 0.34164 | 1.5273 | Parallel | 996.0803 | 1.7607 | 3.175 | 1.7607 | 3.175 | 3.0788 | 4.1974 | 3.6381 | 22.9748 | 31.3223 | 54.2971 | 45.0788 | 50.9659 | 69.4834 | 60.2247
6 |  | 70 | 1260 | 28.6 | 0.65635 | 26.5316 | 37.4623 | 0.34164 | 1.5273 | Parallel | 996.0803 | 1.7607 | 3.175 | 1.7607 | 3.175 | 3.0788 | 4.1974 | 3.6381 | 22.9748 | 31.3223 | 54.2971 | 45.0788 | 50.9659 | 69.4834 | 60.2247
7 |  | 70 | 1260 | 29.55 | 0.80781 | 26.0015 | 37.2099 | 0.34474 | 1.5273 | Parallel | 995.8095 | 1.7607 | 3.175 | 1.7607 | 3.175 | 3.0098 | 4.1571 | 3.5834 | 22.4534 | 31.013 | 53.4664 | 45.4868 | 49.3626 | 68.1802 | 58.7714
8 |  | 70 | 1260 | 28 | 0.60586 | 26.3296 | 37.6643 | 0.34319 | 1.5645 | Parallel | 996.2471 | 1.8035 | 3.2521 | 1.8035 | 3.2521 | 3.0804 | 4.2401 | 3.6602 | 23.5489 | 32.4151 | 55.964 | 45.2828 | 52.004 | 71.5838 | 61.7939
9 |  | 70 | 1260 | 28.6 | 0.65635 | 25.648 | 35.8467 | 0.34474 | 1.5645 | Parallel | 996.0803 | 1.8035 | 3.2521 | 1.8035 | 3.2521 | 3.0059 | 4.0496 | 3.5277 | 22.9757 | 30.9533 | 53.9289 | 45.4868 | 50.5106 | 68.049 | 59.2798
10 |  | 70 | 1260 | 28 | 0.60586 | 26.3296 | 37.6643 | 0.34319 | 1.5645 | Parallel | 996.2471 | 1.8035 | 3.2521 | 1.8035 | 3.2521 | 3.0804 | 4.2401 | 3.6602 | 23.5489 | 32.4151 | 55.964 | 45.2828 | 52.004 | 71.5838 | 61.7939
11 |  | 70 | 1260 | 28.6 | 0.65635 | 25.648 | 35.8467 | 0.34474 | 1.5645 | Parallel | 996.0803 | 1.8035 | 3.2521 | 1.8035 | 3.2521 | 3.0059 | 4.0496 | 3.5277 | 22.9757 | 30.9533 | 53.9289 | 45.4868 | 50.5106 | 68.049 | 59.2798
12 |  | 70 | 1260 | 29.05 | 0.75732 | 26.1782 | 36.4525 | 0.33701 | 1.5645 | Parallel | 995.9531 | 1.8035 | 3.2521 | 1.8035 | 3.2521 | 3.0501 | 4.1017 | 3.5759 | 23.3109 | 31.3478 | 54.6587 | 44.4669 | 52.4231 | 70.4969 | 61.46
13 |  | 70 | 1260 | 29.55 | 0.70684 | 25.648 | 35.9981 | 0.34474 | 1.584 | Parallel | 995.8095 | 1.826 | 3.2927 | 1.826 | 3.2927 | 3.0108 | 4.0703 | 3.5405 | 23.2941 | 31.4913 | 54.7854 | 45.4868 | 51.2108 | 69.2318 | 60.2213
14 |  | 70 | 1260 | 30.95 | 0.65635 | 25.2441 | 36.9574 | 0.35401 | 1.584 | Parallel | 995.3957 | 1.826 | 3.2927 | 1.826 | 3.2927 | 2.9757 | 4.1752 | 3.5754 | 23.0127 | 32.2896 | 55.3023 | 46.7106 | 49.2666 | 69.1268 | 59.1967
15 |  | 70 | 1260 | 28.65 | 0.50488 | 25.3956 | 35.3418 | 0.34783 | 1.6406 | Parallel | 996.0663 | 1.8913 | 3.4105 | 1.8913 | 3.4105 | 3.0328 | 4.0507 | 3.5418 | 24.3099 | 32.4689 | 56.7788 | 45.8947 | 52.9688 | 70.7464 | 61.8576
16 |  | 70 | 1260 | 28.65 | 0.50488 | 25.3956 | 35.3418 | 0.34783 | 1.6406 | Parallel | 996.0663 | 1.8913 | 3.4105 | 1.8913 | 3.4105 | 3.0328 | 4.0507 | 3.5418 | 24.3099 | 32.4689 | 56.7788 | 45.8947 | 52.9688 | 70.7464 | 61.8576
17 |  | 70 | 1260 | 29.6 | 0.60586 | 25.4461 | 35.4933 | 0.34474 | 1.6602 | Parallel | 995.7951 | 1.9138 | 3.4511 | 1.9138 | 3.4511 | 3.0382 | 4.0667 | 3.5524 | 24.636 | 32.976 | 57.612 | 45.4868 | 54.1609 | 72.4958 | 63.3283
18 |  | 70 | 1260 | 28 | 0.45439 | 24.1586 | 35.1903 | 0.35246 | 1.6777 | Parallel | 996.2471 | 1.934 | 3.4876 | 1.934 | 3.4876 | 2.9297 | 4.0585 | 3.4941 | 24.0192 | 33.2733 | 57.2924 | 46.5066 | 51.6467 | 71.5452 | 61.596
19 |  | 70 | 1260 | 28 | 0.45439 | 24.1586 | 35.1903 | 0.35246 | 1.6777 | Parallel | 996.2471 | 1.934 | 3.4876 | 1.934 | 3.4876 | 2.9297 | 4.0585 | 3.4941 | 24.0192 | 33.2733 | 57.2924 | 46.5066 | 51.6467 | 71.5452 | 61.596
20 |  | 70 | 1260 | 30.9 | 0.30293 | 23.6285 | 35.4428 | 0.35556 | 1.6777 | Parallel | 995.4108 | 1.934 | 3.4876 | 1.934 | 3.4876 | 2.893 | 4.1029 | 3.4979 | 23.698 | 33.6086 | 57.3067 | 46.9146 | 50.5132 | 71.6379 | 61.0755
21 |  | 70 | 1260 | 28.65 | 0.25244 | 23.679 | 33.0193 | 0.35092 | 1.6973 | Parallel | 996.0663 | 1.9566 | 3.5282 | 1.9566 | 3.5282 | 2.9118 | 3.8677 | 3.3898 | 24.1457 | 32.0722 | 56.218 | 46.3027 | 52.1476 | 69.2665 | 60.7071
22 |  | 70 | 1260 | 28.65 | 0.25244 | 23.679 | 33.0193 | 0.35092 | 1.6973 | Parallel | 996.0663 | 1.9566 | 3.5282 | 1.9566 | 3.5282 | 2.9118 | 3.8677 | 3.3898 | 24.1457 | 32.0722 | 56.218 | 46.3027 | 52.1476 | 69.2665 | 60.7071
23 |  | 70 | 1260 | 29.6 | 0.40391 | 23.7547 | 35.1903 | 0.35092 | 1.6973 | Parallel | 995.7951 | 1.9566 | 3.5282 | 1.9566 | 3.5282 | 2.9047 | 4.0753 | 3.49 | 24.0803 | 33.7849 | 57.8652 | 46.3027 | 52.0063 | 72.9654 | 62.4858
24 |  | 70 | 1260 | 29.65 | 0.30293 | 23.9062 | 34.2311 | 0.35401 | 1.6973 | Parallel | 995.7806 | 1.9566 | 3.5282 | 1.9566 | 3.5282 | 2.9306 | 3.9875 | 3.4591 | 24.2945 | 33.0565 | 57.3509 | 46.7106 | 52.0106 | 70.7687 | 61.3896
25 |  | 70 | 1260 | 28.9 | 0.45439 | 23.2751 | 34.1301 | 0.33855 | 1.7168 | Parallel | 995.9957 | 1.9791 | 3.5688 | 1.9791 | 3.5688 | 2.8601 | 3.9711 | 3.4156 | 23.9885 | 33.3064 | 57.2949 | 44.6709 | 53.7006 | 74.5596 | 64.1301
1 |  | 70 | 1260 | 29 | 0.30293 | 23.8052 | 34.8369 | 0.34164 | 1.7168 | Parallel | 995.9673 | 1.9791 | 3.5688 | 1.9791 | 3.5688 | 2.93 | 4.0591 | 3.4945 | 24.5735 | 34.043 | 58.6165 | 45.0788 | 54.5122 | 75.519 | 65.0156
2 |  | 70 | 1260 | 29.7 | 0.35342 | 23.1994 | 33.9281 | 0.35401 | 1.7168 | Parallel | 995.766 | 1.9791 | 3.5688 | 1.9791 | 3.5688 | 2.8633 | 3.9616 | 3.4124 | 24.0092 | 33.2187 | 57.2279 | 46.7106 | 51.3998 | 71.116 | 61.2579
3 |  | 70 | 1260 | 27.95 | 0.40391 | 23.3256 | 35.2408 | 0.35401 | 1.7344 | Parallel | 996.2609 | 1.9993 | 3.6053 | 1.9993 | 3.6053 | 2.8791 | 4.0983 | 3.4887 | 24.4013 | 34.734 | 59.1353 | 46.7106 | 52.2393 | 74.36 | 63.2997
4 |  | 70 | 1260 | 28.75 | 0.35342 | 23.7042 | 34.7864 | 0.35401 | 1.7344 | Parallel | 996.0381 | 1.9993 | 3.6053 | 1.9993 | 3.6053 | 2.9236 | 4.0577 | 3.4906 | 24.7724 | 34.3828 | 59.1552 | 46.7106 | 53.0338 | 73.608 | 63.3209
5 |  | 70 | 1260 | 27.95 | 0.40391 | 23.3256 | 35.2408 | 0.35401 | 1.7344 | Parallel | 996.2609 | 1.9993 | 3.6053 | 1.9993 | 3.6053 | 2.8791 | 4.0983 | 3.4887 | 24.4013 | 34.734 | 59.1353 | 46.7106 | 52.2393 | 74.36 | 63.2997
6 |  | 70 | 1260 | 28.75 | 0.35342 | 23.7042 | 34.7864 | 0.35401 | 1.7344 | Parallel | 996.0381 | 1.9993 | 3.6053 | 1.9993 | 3.6053 | 2.9236 | 4.0577 | 3.4906 | 24.7724 | 34.3828 | 59.1552 | 46.7106 | 53.0338 | 73.608 | 63.3209
7 |  | 70 | 1260 | 29.7 | 0.35342 | 23.3508 | 34.534 | 0.35401 | 1.7344 | Parallel | 995.766 | 1.9993 | 3.6053 | 1.9993 | 3.6053 | 2.888 | 4.0328 | 3.4604 | 24.4647 | 34.1626 | 58.6273 | 46.7106 | 52.3751 | 73.1367 | 62.7559
8 |  | 70 | 1260 | 30.8 | 0.20195 | 23.2246 | 34.3825 | 0.35865 | 1.7344 | Parallel | 995.4409 | 1.9993 | 3.6053 | 1.9993 | 3.6053 | 2.8914 | 4.034 | 3.4627 | 24.4851 | 34.1611 | 58.6463 | 47.3225 | 51.7409 | 72.1879 | 61.9644
9 |  | 70 | 1260 | 33.45 | 0.50488 | 23.5023 | 35.0389 | 0.35865 | 1.7539 | Parallel | 994.6138 | 2.0219 | 3.6459 | 2.0219 | 3.6459 | 2.9011 | 4.0835 | 3.4923 | 24.8238 | 34.9409 | 59.7647 | 47.3225 | 52.4567 | 73.8356 | 63.1461
65.0156